## Slide 1: Reactors
The Case of the Chlorine Contact Tank

## Slide 2
Reactor Characteristics:
Designing a Chlorine Contact Tank
DI Water
Peristaltic Pump
reactor
baffle
Photometer
P
open tee
drain

## Slide 3: Outline
Objectives of chlorine contact tanks
Reactors in environmental engineering
Advection, dispersion, and reaction
Tracer studies and reactor characterization
Data analysis and curve fitting
Experimental design and ideas to probe

## Slide 4: Chlorine Contact Tanks
Widely employed in water and wastewater plants as the last step in the treatment process
Takes place in a “clearwell” or “contact tank”
Key design parameter: contact time
Notes: What do you notice about these tanks?

## Slide 5: Disinfection CT Credits
Contact time (min)
chlorine pH 6.5 pH 7.5
(mg/L) 2°C 10°C 2°C 10°C
0.5 300 178 430 254
1 159 94 228 134
To get credit for 99.9% inactivation of Giardia:
Inactivation is a function of _______, ____________
______, and ___________.
concentration
time
pH
temperature

## Slide 6: Contact Time Definition
The contact time for purposes of chlorine disinfection is defined by the EPA as
  The time that it takes for 10% of the mass of a tracer pulse to arrive at the effluent of the tank
  Or equivalently, the time it takes for the effluent concentration to reach 10% of the influent concentration after a tracer is added continuously to the influent

## Slide 7: EPA Contact Time Credit
Baffling Condition | Baffle Factor (BF) | Extent of Baffles | Typical Unit Processes
Unbaffled (CMFR) | 0.1 | No baffles, agitated basin with low length to width ratio, high inlet and outlet flow velocities | Clearwell, storage tank, no perforated inlet or outlet, inlet or outlet submerged.
Poorly baffled | 0.3 | Single or multiple unbaffled inlets and outlets, no intrabasin baffles | Many conventional sedimentation basins. Storage tanks with two or three baffles.
Average | 0.5 | Baffled inlet or outlet with some intrabasin baffles | Some (few) sedimentation basins. Highly baffled storage tanks.
Superior | 0.7 | Perforated inlet baffles, serpentine or perforated intrabasin baffles, outlet weir or perforated launders | Filters. Contact tanks with serpentine baffling
Perfect (PFR) | 1.0 | Very high length to width ratio (pipeline flow), perforated inlet, outlet and intrabasin baffles | Sections of pipe ten times longer than their diameter.
Contact time = (baffle factor)(hydraulic residence time)
Notes: How much better than a CMFR is a PFR? 10x! That’s 10 times smaller, 10 times cheaper!

## Slide 8: The Meaning of Life… for Contact Tanks
Minimally – To meet EPA regulations
Better – To obtain as high a contact time as possible with a given tank
Or – To build as small a tank as possible that meets the EPA regulations

## Slide 9: Reactors
Reactor: a “container” where a reaction occurs
Examples:
  Clear well at water treatment plant (chlorine contact)
  Activated sludge tank at wastewater treatment plant
  Treated wastewater discharge into a stream: stream = reactor
  Treated wastewater discharge into Cayuga lake: lake = reactor
  Gas tank leaking into soil: soil = reactor
Notes: Environmental Engineers are interested in knowing the effects of various inputs into our environment. When we model the environment we often draw a boundary around the part of the environment we want to study and call it a control volume or a reactor.
Environmental Engineers also design reactors in the more conventional sense in treatment plants for water, wastewater, contaminated site remediation...)

## Slide 10: Advection: mean flow
What does it look like a short time later?
x
C
x
C
Notes: where concentration is increasing with x it will decrease with time given positive velocity
C
x
t = 0
t = t1
ut1

## Slide 11: Dispersion: velocity fluctuations
Fick's first law
Fick's second law
What does it look like a short time later?
x
C
x
C
Notes: C
x
t = 0
0
0
0
+
+
-
-
2nd derivatives
C
x
t = 0
0
0
0
+
-
1st derivatives
Change in concentration with time at second derivatives
Flux is in negative direction when concentration is increasing with x
t = t1
C
x
t = 0

## Slide 12: Reaction
What does it look like a short time later?
x
C
x
C
Notes: C
x
t = 0
t = t1

## Slide 13: Advection/Dispersion/Reaction
In three dimensions
where
x
C
x
C

## Slide 14: Reactors: Closed vs. Open
Closed: have little dispersion across the inlet and outlet boundaries
  Well defined reactor volume
  Examples
    __________________________________
    ______
Open: have significant dispersion across the inlet and outlet boundaries
  Backmixing
  Example
    _______
tank with a small inlet and a small outlet
lake
river

## Slide 15: Reactors: Defining the Control Volume
Q
Q
tracer
closed
open

## Slide 16: Reactor Characterization
Time scales
  hydraulic residence time
  average time for tracer to get from inlet to outlet
Closed systems
  “dead volume”
Open systems
  dispersion upstream
  “dead volume”
volume
flow rate
=
?
Notes: Why 2 time scales?
theta assumes fluid is flowing through entire reactor volume
How is theta measured? (volume and flow rate)
tbar
what is the average time that a molecule spends in the reactor?
how many of the molecules present at time zero are leaving at time t? proportional to t*C(t)
How is t bar measured? (concentration measurements as a function of time)

## Slide 17: Peclet Number
Ratio of advection to dispersion
  how far does advection carry the fluid/width of tracer plume
High Peclet means primarily advection (_______________)
Low Peclet means lots of mixing
plug flow

## Slide 18: Characterize a Tank: Tracer Studies
Tracers
  Desirable properties
  Candidates
  Measuring techniques
Choosing a tracer concentration
  Measurement range
  Interferences
Density matching
Pulse vs. Step
Requires design calculations!
Crucial for high Pe!

## Slide 19: Ideal Tracer
same properties as fluid
  viscosity
  temperature
  density
  non reactive
additional properties
  low background concentrations
  easily measured
  cheap
  non toxic

## Slide 20: Real Tracers
Tracer type
distinguishing
property
analytical
instrument
examples
salt
conductivity
Conductivity
meter
NaCl
Dyes
color
Spectrophoto-
meter
methylene blue
fluorescent
dye
fluorescence
Fluorometer
rhodamine WT
acid
protons
pH probe
HCl
Dissolved gas
Gas
Gas
chromatograph
Sulfur
hexafluoride

## Slide 21: Reactor Theory: CMFR
Chart: t*
t* at F=0.1 | 0 | 0.1 | 0.1
r = reactor
tr = tracer
t = time
Dimensionless groups

## Slide 22: E and F curves
The E curve is a dimensionless measure of the output tracer concentration from a spike input.
The F curve is a dimensionless measure of the cumulative output from a spike input
The F curve is also a dimensionless measure of the output tracer concentration from a step input

## Slide 23: Reactor Theory: Series CMFR
Chart: t*
t* at F=0.1 | 0 | 0.1 | 0.1
Chart: t*
t* at F=0.1 | 0 | 0.1 | 0.1
Chart: t*
t* at F=0.1 | 0 | 0.1 | 0.1
N=2
N=20
N=100
N must be an integer!
Residence time is for total reactor

## Slide 24: Gamma Function to Replace Factorial?
We will be using solver to find N. It would be better if we had a continuous function rather than one that only works for whole numbers
The (complete) gamma function is defined to be an extension of the factorial to complex and real number arguments. It is related to the factorial by
Notes: http://mathworld.wolfram.com/GammaFunction.html

## Slide 25: G(x+1)
Chart: x
factorial (x) | 1 | 1 | 2 | 6 | 24 | 120 | 720 | 5040 | 40320 | 362880 | 3628800

## Slide 26: 1-D Dispersion
0
20
40
60
80
100
120
-0.1
-0.05
0
distance (cm)
concentration (g/mL)
0.05
0.1
1 s
10 s
100 s
A
Dm = 0.673 x 10-5 cm2/s
M = 1 g
A = 1 cm2
Symmetric in space
No boundaries in x!
Notes: What happens when we add advection to dispersion? Dispersion continues while advection happens!

## Slide 27: 1-D Advective Dispersion Equation
Chart: t*
t* at F=0.1 | 0 | 0.1 | 0.1
Pe = 2
Note: This reactor has more dispersion than a series CMFR with N = 2, but it has a longer contact time!
advection
dispersion
skewed in time

## Slide 28: 1-D Advective Dispersion Extremes: High Dispersion
How can it take 1.9 residence times for 10% of the tracer to come out?
Why is the contact time so good?
Why is F so small at 3 residence times?
Hey! That’s not fair!
Chart: t*
t* at F=0.1 | 0 | 0.1 | 0.1
(Pe = 0.02)
Open reactor!

## Slide 29: 1-D Advective Dispersion Extremes: Low Dispersion
________________________________________________________________
Approaches plug flow!
Chart: t*
t* at F=0.1 | 0 | 0.1 | 0.1
(Pe = 2000)
Characteristic of flow through homogeneous porous media

## Slide 30: CMFR in series ≡ Advective Dispersion
Chart: t*
t* at F=0.1 | 0 | 0.1 | 0.1
Chart: t*
t* at F=0.1 | 0 | 0.1 | 0.1
(Pe = 100)
(N = 50)
They both approach plug flow!
For Pe > 100!
What is Pe for a porous media column?
Notes: How many reactors in series? Think sand grain pores. Thus N is something like height of filter/sand grain diameter. And Pe is 2*N. Thus for a 20 cm deep filter with 0.5 mm sand grains we have 400 reactors and Pe of 800!

## Slide 31: Goals of plug flow without dead volume
Many CMFR in series
High Peclet number
  Laminar pipe flow
  Turbulent pipe flow
  Porous media flow
Eliminating “Dead volume”
  Requires more mixing!
  Turbulent pipe flow: Serpentine channels
  Turbulent jets: Perforated baffles
Closed reactors
Open reactors
?

## Slide 32: Serpentine Chlorine Contact Tanks
Baffle Factor of________.
0.5
Model as_________________.
flow with dispersion

## Slide 33: Distribution Tank (Honduras)
How would you model this tank?
__________
_______________________________________________________________________
Baffle Factor of________.
0.1
CMFR!
The water flowing from the inlet pipe provides enough energy to mix the tank!

## Slide 34: Experiment Design Options
Baffles
  With holes
    (pattern, diameter, number)
    Head loss
    Jet Reynolds number
  Partial baffles
Reactor flow rate
Reactor depth
Porous media
  Packing material
Mean circulation patterns
Serpentine vs. series CMFR
  Risk of dead volumes

## Slide 35: Mass Conservation
What is the purpose of checking mass conservation? _______________________
Four ways to check
At infinity…
At all times
dimensionless
Verify measurement accuracy

## Slide 36: Characteristic times…
What is the difference between q and ?
is only defined correctly if all of the tracer is accounted for!!!!!!!
What does it mean if q is greater than ?
What does it mean if q is less than ?
What other technique could you use to measure the tracer residence time?
Curve fit with models
Dead volume
Open reactor?

## Slide 37: Comparison with Models
Which model do you expect might describe perforated baffle reactors?
Which model do you expect might describe serpentine reactors?

## Slide 38: Estimating the Peclet number (or the number of CMFR in series)
Use multiple variable regression analysis.
Minimize the SSE (sum of the squared errors) between the model and the data by changing ( and ) and (Pe or N) (use EPA.Solver)
model
data
Requires data from the entire tracer curve
Notes: Why are there 3 parameters that we get to play with? Mean time, spread, amplitude

## Slide 39: Data Analysis Requirements: 2 goals
Measure the baffle factor
  Can be as simple as finding the time when 10% of the tracer gets to the effluent
Compare the data with the two reactor models
  At minimum requires fitting N or Pe
  But there is no reason to expect the hydraulic residence time to be the same as the tracer residence time – so fit and too.

## Slide 40: Organizing Experiments
Protocol for sharing resources? (baffles)
What is the question you are trying to answer?
Make sure you conduct experiments that provide data to answer that question!
Jet Reynolds number is not an important parameter, but head loss is!
Only vary one parameter at a time!!!!
Distilled water
How do you choose and control reactor volume?
USE YOUR EYES!!!!!

## Slide 41: Do an additional set of experiments
Vary a different parameter over at least 3 values
Effect of depth given serpentine path
Baffles in the long direction
Turbulent pipe flow
Porous media flow
Effect of Reynolds number (can you get the transition between laminar and turbulent flow in open channel flow)?
Inlet and outlet conditions matter!